## Sheet2
| Value in hex |  | Enable/Disable | Auto reset | Trip relay 1 | Alarm relay 2 | trip setting | Alarm delay | trip delay
start bit pos |  |  | 0 | 1 | 3 | 5 | 7 | 17 | 24
No of bit |  |  | 1 | 2 | 2 | 2 | 10 | 7 | 8
range value(in dec) |  |  | 0-1 | 0-3 | 0-3 | 0-3 | 0-1023 | 0-127 | 0-255
default value(in dec) |  |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
equivalent value as per shift position(in dec) |  |  | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
equivalent value as per shift position(in hex) | 50A0A2B
parameter |  | value in hex
Under Voltage | default val |  | 1 | 3 | 3 | 3 | 50 | 50 | 5
| value as per shift position | 564197F | 1 | 6 | 24 | 96 | 6400 | 6553600 | 83886080
Over Voltage | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Phase failure | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Unbalance | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Phase Reversal | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Under current | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Over current | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Inverse time Overload | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Current Unbalance | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Rotor Jam/ Stall | default val |  | 1 | 1 | 1 | 1 | 800 | 5 | 5
| value as per shift position | 50B902B | 1 | 2 | 8 | 32 | 102400 | 655360 | 83886080
Prolonged start | default val |  | 1 | 1 | 1 | 1 | 400 | 5 | 5
| value as per shift position | 50AC82B | 1 | 2 | 8 | 32 | 51200 | 655360 | 83886080
Phase failure | default val |  | 1 | 1 | 1 | 1 | 50 | 5 | 5
| value as per shift position | 50A192B | 1 | 2 | 8 | 32 | 6400 | 655360 | 83886080
Phase reversal | default val |  | 1 | 1 | 0 | 0 | 0 | 0 | 0
| value as per shift position | 3 | 1 | 2 | 0 | 0 | 0 | 0 | 0
Under Power | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Over power | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Ground fault (ELR) | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
PTC Over temp | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Earth fault | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Contactor Failure | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Power-up timer | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Rapid-cycle timer | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Underload restart timer | default val |  | 1 | 1 | 1 | 1 | 20 | 5 | 5
| value as per shift position | 50A0A2B | 1 | 2 | 8 | 32 | 2560 | 655360 | 83886080
Note on A48: RD0 is referred to as the power-up timer, in seconds. The purpose of this timer is to provide protection against power system fluctuations. The purpose of this timer is to delay the start of a motor for a period of time after good power returns. Each motor in a multimotor environment should have this set to different values to allow each motor to start at different times after power returns to normal to avoid overloading the power system. This ensures that no two motors will be drawing startup current levels at the same time. This timer is initiated when acceptable power is applied to the L1, L2, L3 terminals, and will also be reloaded if the incoming power does not meet the LV, HV, or VUB settings when the motor is not running. When power returns to within these settings, the RD0 timer will count down and close the relay. If RD0 timer is set to 0, this timer will be disabled.
Note on A50: RD1 is referred to as the rapid-cycle timer, in seconds. The purpose of this timer is to provide protection against short cycling of the controls between motor starts. This timer is initiated after the motor has been stopped by breaking the control power. At this time the control relay is opened and the output relay will energize (the NO will close) as soon as RD1 timer expires. If RD1 is set to zero this delay will be disabled.
Note on A52: RD3 is referred to as the underload restart timer, in seconds. RD3 is used to restart the motor after an operating motor trips due to UC or LKW. An example of the use of this timer is to set it to the period of time required for a well to recover. This setting varies widely by application and there is no typical setting.

## Sheet1
parameter | start bit pos | No of bit | range value(in dec) | default value | value in decimal | value euivalent to shift position
Enable/Disable | 0 | 1 | 0-1 | 1 | 1 | 1
Auto reset | 1 | 2 | 0-3 | 1 | 01 | 2
Trip relay 1 | 3 | 2 | 0-3 | 1 | 01 | 8
Alarm relay 2 | 5 | 2 | 0-3 | 1 | 01 | 32
trip setting | 7 | 10 | 0-1023 | 20 | 0000010100 | 1292800
Alarm delay | 17 | 7 | 0-127 | 5 | 0000101 | 13238272
trip delay | 24 | 8 | 0-255 | 5 | 00000101 | 1694498816
|  | 32 |  |  |  | 65DDBA2B