## Trip setup
Deafult
Class | Parameter | Enable/ Disable | Auto reset | Relay 1 | Relay 2 | Trip code | Trip Setting range | Alarm setting range | Time delay range | Mode of Setting | Relay 1 | Relay 2 | Auto Reset | Trip Setting range | Time delay range | Trip Accuracy | 485 Address | 485 number format | 485 R/w
Voltage | Under Voltage | Y | Y/N | Trip/ disable | Trip/ alarm/ disable | UV | (20-100%)of Nominal voltage | (50-95%)>UV | 0.03-60 | BT | Trip | disable | Y | 20% | 5 | 90-100% |  |  | R/W
| Over Voltage | Y | Y/N | Trip/ disable | Trip/ alarm/ disable | OV | (20-100%)of Nominal voltage | (50-95%)<OV | 0.03-60 | BT | Trip | disable | Y | 20% | 5 | 90-100% |  |  | R/W
| Phase failure | N | Y/N | Trip | NA | PL-U | N/A | immediately | immediately | BT | Trip | Trip | Y | 50% | immediately | 90-100% |  |  | R/W
| Unbalance | Y | Y/N | Trip/ disable | Trip/ alarm/ disable | VU | (5-80%)(high-low)/high | (50-95%)of VU | 0.03-120 | BT | Trip | disable | Y | 20% | 5 | 90-100% |  |  | R/W
| Phase Reversal | N | Y/N | Trip | NA | Pr | N/A | immediately | immediately | BT | Trip | Trip | Y | 0 | immediately | 90-100% |  |  | R/W
Current | Under current | Y | Y/N | Trip/ disable | Trip/ alarm/ disable | UC | (10-100%)of rated current | (50-95%)o>UC | 0.03-60 | BT | Trip | disable | N | 20% | 5 | 90-100% |  |  | R/W
| Over current | Y | NA | Trip/ disable | Trip/ alarm/ disable | OC | (10-100%)of rated current | (50-95%)<OC | 0.03-60 | BT | Trip | disable |  | 20% | 5 | 90-100% |  |  | R/W
| Inverse time Overload | Y | NA | Trip/ disable | Trip/ alarm/ disable | OL |  | (50-95%)OL | 0.03-60 | BT | Trip | disable |  | 110% | 5 | 90-100% |  |  | R/W
| Current Unbalance | Y | NA | Trip/ disable | Trip/ alarm/ disable | CU | (5-80%)(high-low)/high | (50-95%)of CU | 0.03-120 | BT | Trip | disable |  | 20% | 5 | 90-100% |  |  | R/W
| Rotor Jam/ Stall | Y | NA | Trip/ disable | Trip/ alarm/ disable | rJ | (800-1000%)of rated current | (50-95%)<rJ | 0.03-60 | BT | Trip | disable |  | 800% | 5 | 90-100% |  |  | R/W
| Prolonged start | Y | NA | Trip/ disable | Trip/ alarm/ disable | PS | (400-800%)of rated current | (50-95%)<PS | 0.03-60 | BT | Trip | disable |  | 400% | 5 | 90-100% |  |  | R/W
| Phase failure | N | NA | Trip | NA | PL-C | N/A | immediately | immediately | BT | Trip | Trip |  | 50% | immediately | 90-100% |  |  | R/W
| Phase reversal | N | NA | Trip | NA | Pr | N/A | immediately | immediately | BT | Trip | Trip |  | 0 | immediately | 90-100% |  |  | R/W
Power | Under Power | Y | Y/N | Trip/ disable | Trip/ alarm/ disable | UP | (10-60%) of rated power | (50-95%)>UP | 0.03-60 | BT | Trip | disable | N | 20% | 5 | 90-100% |  |  | R/W
| Over power | Y | NA | Trip/ disable | Trip/ alarm/ disable | OP | (80-200%) of rated power | (50-95%)<OP | 0.03-60 | BT | Trip | disable |  | 20% | 5 | 90-100% |  |  | R/W
Misc | Ground fault (ELR) | Y | NA | Trip/ disable | Trip/ alarm/ disable | G-F | (0.03-3)A | (50-95%)G-F | 0.03-60 | BT | Trip | disable |  | 20% | 5 | 90-100% |  |  | R/W
| PTC Over temp | Y | NA | Trip/ disable | Trip/ alarm/ disable | P-tp |  |  |  | BT | Trip | disable |  |  | 5 | 90-100% |  |  | R/W
| Earth fault | Y | NA | Trip/ disable | Trip/ alarm/ disable | E-F | 5-20% FLA | (50-95%)G-F | 0.03-60 | BT | Trip | disable |  | 200% | 5 | 90-100% |  |  | R/W
Others | Contactor Failure | Y | NA | Trip/ disable | NA | CT-F |  |  | 0.03-60 | BT | Trip | disable |  |  | 5 | 90-100% |  |  | R/W
Timers | Power-up timer | Y | NA | Trip/ disable | NA | PU-t | 1-120sec |  | 0.03-120 | BT | Trip | disable |  | 5 | 5 | 90-100% |  |  | R/W
| Rapid-cycle timer | Y | NA | Trip/ disable | NA | RC-t |  |  | 0.03-60 | BT | Trip | disable |  | 5 | 5 | 90-100% |  |  | R/W
| Underload restart timer |  | NA |  | NA |  |  |  |  | BT
| Cool-down timer | Y | NA | Trip/ disable | NA | CL-t | 1-240 sec |  | 0.03-60 | BT | Trip | disable |  | 60 | 5 | 90-100% |  |  | R/W
Nominal voltage
Nominal Current
184
Note on B3: Under_vol[5]=(en_Dis, relay1.......)
Note on E3: Trip = 1; Disable=0
Note on N3: <=Set value or 3% Hysteresis from the trip value -> whichever lower
Note on B4: tasas
Note on N4: <=Set value or 3% Hysteresis from the trip value -> whichever lower
Note on N5: <=Set value or 3% Hysteresis from the trip value -> whichever lower
Note on N6: <=Set value or 3% Hysteresis from the trip value -> whichever lower
Note on N7: <=Set value or 3% Hysteresis from the trip value -> whichever lower
Note on N8: Restart after Underload restart timer delay
Note on N16: Restart after Underload restart timer delay
Note on B21: The unit has tripped on current single-phasing, but was not single-phased by the incoming voltage. Check for damaged contacts or loose or corroded wiring connections.
Note on B22: RD0 is referred to as the power-up timer, in seconds. The purpose of this timer is to provide protection against power system fluctuations. The purpose of this timer is to delay the start of a motor for a period of time after good power returns. Each motor in a multimotor environment should have this set to different values to allow each motor to start at different times after power returns to normal to avoid overloading the power system. This ensures that no two motors will be drawing startup current levels at the same time. This timer is initiated when acceptable power is applied to the L1, L2, L3 terminals, and will also be reloaded if the incoming power does not meet the LV, HV, or VUB settings when the motor is not running. When power returns to within these settings, the RD0 timer will count down and close the relay. If RD0 timer is set to 0, this timer will be disabled.
Note on B23: RD1 is referred to as the rapid-cycle timer, in seconds. The purpose of this timer is to provide protection against short cycling of the controls between motor starts. This timer is initiated after the motor has been stopped by breaking the control power. At this time the control relay is opened and the output relay will energize (the NO will close) as soon as RD1 timer expires. If RD1 is set to zero this delay will be disabled.
Note on B24: RD3 is referred to as the underload restart timer, in seconds. RD3 is used to restart the motor after an operating motor trips due to UC or LKW. An example of the use of this timer is to set it to the period of time required for a well to recover. This setting varies widely by application and there is no typical setting.
Note on B25: RD2 is referred to as the motor cool-down timer, in seconds. RD2 is used to restart the motor after an operating motor trips due to OC, CUB, or HKW.

## Trip setup data frame
Protocol
|  | Data frame For Individual |  |  |  |  | Data frame For All
Parameters | Address/ID | address | length | data | data type |  | address | length | data | data type
|  | 2 bytes | 1 bytes | 4 bytes |  |  |  | 2+total_no_pra*data_size+1
Under Voltage | 1001 |  | 7 |  | uint32_t |  | 1000 | 95 | 92 | array of uint32_t
Over Voltage | 1002 |  | 7 |  | uint32_t
Phase failure | 1003 |  | 7 |  | uint32_t
Unbalance | 1004 |  | 7 |  | uint32_t
Phase Reversal | 1005 |  | 7 |  | uint32_t
Under current | 1006 |  | 7 |  | uint32_t
Over current | 1007 |  | 7 |  | uint32_t
Inverse time Overload | 1008 |  | 7 |  | uint32_t
Current Unbalance | 1009 |  | 7 |  | uint32_t
Rotor Jam/ Stall | 1010 |  | 7 |  | uint32_t
Prolonged start | 1011 |  | 7 |  | uint32_t
Phase failure | 1012 |  | 7 |  | uint32_t
Phase reversal | 1013 |  | 7 |  | uint32_t
Under Power | 1014 |  | 7 |  | uint32_t
Over power | 1015 |  | 7 |  | uint32_t
Ground fault (ELR) | 1016 |  | 7 |  | uint32_t
PTC Over temp | 1017 |  | 7 |  | uint32_t
Earth fault | 1018 |  | 7 |  | uint32_t
Contactor Failure | 1019 |  | 7 |  | uint32_t
Power-up timer | 1020 |  | 7 |  | uint32_t
Rapid-cycle timer | 1021 |  | 7 |  | uint32_t
Underload restart timer | 1022 |  | 7 |  | uint32_t
Cool-down timer | 1023 |  | 7 |  | uint32_t
Data details and aliangment
Time Delay | [7 empty] | alarm range | [6 empty] | Trip setting | [9 empty] | Alarm relay
31 | 30 | 29 | 28 | 27 | 26 | 25 | 24 | 23 | 22 | 21 | 20 | 19 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6
Alarm relay | trip relay 1 |  | Auto reset |  | Enable/Disable
5 | 4 | 3 | 2 | 1 | 0

## Display Setup
| Display/ Setup | Min /Max setting | 485 Address | 485 number format | 485 R/w | BT R/W | Option 1 | Option 2 | Option 3
Time | BT |  |  |  | Read only | R/W
Date | BT |  |  |  | Read only | R/W
Current range | BT | 0.6-6(CT driven) / 2-20(Direct ) / 6-80A(Direct ) |  |  | Read only | Read only
CT Primary | BT | 0.6-6A(ext CT) |  |  | Read only | R/W | CT driven possiblity only if 0.6-6A
CT Secondary | BT | 50-5000A |  |  | Read only | R/W | CT driven possiblity only if 0.6-6A
FLA | BT |  |  |  | Read only | R/W | 2-20A | 6-80A | 30% to 100% of CT sec setting(ext CT)
Voltage Setting | BT | Direct / PT driven |  |  | Read only | R/W
PT Primary | BT |  |  |  | Read only | R/W | 90-140
PT Secondary | BT |  |  |  | Read only | R/W | 1kv - 20kv
Nominal voltage | BT |  |  |  | Read only | R/W | 180 - 480 V | 70% to 100% of PT Sec |  | This option 1/2 is dependent on PT setting PT= 90-14V and Direct = 180-480V
KVA rating of motor | BT |  |  |  | Read only | Read only | kVA = Nominal voltage x FLA
Motor rating in kW | BT |  |  |  | Read only | R/W | 50 to 100% of the KVA rating of motor.
MD rolling window time | BT | 0=off, 10, 15, 30 or 60 minutes |  |  | Read only | R/W

## Display setup data frame
Protocol
Data frame
Parameters | Address/ID | address | length | data | data Type | Range
|  | 2 bytes | 1 bytes | 4 bytes/2 bytes
Time | 2001 |  | 7 | 4 | uint32_t | (0-23):(0-59):(0-59)(1 bytes each)
Date | 2002 |  | 5 | 2 | uint16_t | 2000-2099
Current range | 2003 |  | 5 | 2 | uint16_t | 0.6-80A
CT Primary | 2004 |  | 7 | 2 | uint16_t | 0.6-6A
CT Secondary | 2005 |  | 7 | 2 | uint16_t | 50-5000A
FLA | 2006 |  | 5 | 2 | uint16_t | 2-80A
Voltage Setting | 2007 |  | 5
PT Primary | 2008 |  | 5 | 2 | uint16_t | 90-140V
PT Secondary | 2009 |  | 5 | 2 | uint16_t | 1KV-20KV
Nominal voltage | 2010 |  | 5 | 2 | uint16_t | 180-480V
KVA rating of motor | 2011 |  | 5 | 2 | uint16_t | 360 to 40KVA
Motor rating in kW | 2012 |  | 5 | 2 | uint16_t | 360 to 40KW
MD rolling window time | 2013 |  | 5 | 2 | uint16_t | 0,10,15,30,60
Data frame for ALL
| address | length | data | data Type
| 2000 | 31 | 28

## Measured data frame
|  |  | data frame for individual |  |  |  | data frame for all
| Parameters | Address/ID | address | length | data | data Type | address | length | data | data Type
[6 empty] | float32_t |  |  |  | float32_t
Vol | RY | 3001 |  | 7 |  |  | 3000 | 387 | 384
| YB | 3002 |  | 7
| BR | 3003 |  | 7
Current | R | 3004 |  | 7
| Y | 3005 |  | 7
| B | 3006 |  | 7
Power | kW | 3007 |  | 7
| kVA | 3008 |  | 7
| kVAr | 3009 |  | 7
| P.F. | 3010 |  | 7
| MD kW | 3011 |  | 7
| MD kVA | 3012 |  | 7
Energy | kWh | 3013 |  | 7
| kVAh | 3014 |  | 7
Misc | % thermal | 3015 |  | 7
| % load bargraph | 3016 |  | 7
| Leakage (mA) | 3017 |  | 7
| Freq | 3018 |  | 7
| Motor status | 3019 |  | 7
| Trip counter | 3020 |  | 7
| Stop counter | 3021 |  | 7
| Start counter | 3022 |  | 7
| Time | 3023 |  | 7
| Date | 3024 |  | 7
| Time | (HH:MM:SEC)
1 bytes each
Note on B20: This % kW of the rated load

## Comunication plan
|  | SLNO | Trip setup | address of parameter | display setup | address of parameter | measured | address of parameter | fault parameter | address of parameter
communications ID(2 bytes) | start address | 1 | Under Voltage | 1001 | Time | 2001 | RY | 3001 | Under Voltage | 4001
Trip setup parameter | 1000 | 2 | Over Voltage | 1002 | Date | 2002 | YB | 3002 | Over Voltage | 4002
display setup parameter | 2000 | 3 | Phase failure | 1003 | Current range | 2003 | BR | 3003 | Phase failure | 4003
measured parameter | 3000 | 4 | Unbalance | 1004 | CT Primary | 2004 | R | 3004 | Unbalance | 4004
fault parameter | 4000 | 5 | Phase Reversal | 1005 | CT Secondary | 2005 | Y | 3005 | Phase Reversal | 4005
|  | 6 | Under current | 1006 | FLA | 2006 | B | 3006 | Under current | 4006
|  | 7 | Over current | 1007 | Voltage Setting | 2007 | kW | 3007 | Over current | 4007
|  | 8 | Inverse time Overload | 1008 | PT Primary | 2008 | kVA | 3008 | Inverse time Overload | 4008
|  | 9 | Current Unbalance | 1009 | PT Secondary | 2009 | kVAr | 3009 | Current Unbalance | 4009
|  | 10 | Rotor Jam/ Stall | 1010 | Nominal voltage | 2010 | P.F. | 3010 | Rotor Jam/ Stall | 4010
|  | 11 | Prolonged start | 1011 | KVA rating of motor | 2011 | MD kW | 3011 | Prolonged start | 4011
|  | 12 | Phase failure | 1012 | Motor rating in kW | 2012 | MD kVA | 3012 | Phase failure | 4012
|  | 13 | Phase reversal | 1013 | MD rolling window time | 2013 | kWh | 3013 | Phase reversal | 4013
|  | 14 | Under Power | 1014 |  |  | kVAh | 3014 | Under Power | 4014
|  | 15 | Over power | 1015 |  |  | % thermal | 3015 | Over power | 4015
|  | 16 | Ground fault (ELR) | 1016 |  |  | % load bargraph | 3016 | Ground fault (ELR) | 4016
|  | 17 | PTC Over temp | 1017 |  |  | Leakage (mA) | 3017 | PTC Over temp | 4017
|  | 18 | Earth fault | 1018 |  |  | Freq | 3018 | Earth fault | 4018
|  | 19 | Contactor Failure | 1019 |  |  | Motor status | 3019 | Contactor Failure | 4019
|  | 20 | Power-up timer | 1020 |  |  | Trip counter | 3020 | Power-up timer | 4020
|  | 21 | Rapid-cycle timer | 1021 |  |  | Stop counter | 3021 | Rapid-cycle timer | 4021
|  | 22 | Underload restart timer | 1022 |  |  | Start counter | 3022 | Underload restart timer | 4022
|  | 23 | Cool-down timer | 1023 |  |  | Time | 3023 | Cool-down timer | 4023
[7 empty] | Date | 3000
Note on D2: Under_vol[5]=(en_Dis, relay1.......)
Note on D3: tasas
Note on J17: This % kW of the rated load
Note on D20: The unit has tripped on current single-phasing, but was not single-phased by the incoming voltage. Check for damaged contacts or loose or corroded wiring connections.
Note on D21: RD0 is referred to as the power-up timer, in seconds. The purpose of this timer is to provide protection against power system fluctuations. The purpose of this timer is to delay the start of a motor for a period of time after good power returns. Each motor in a multimotor environment should have this set to different values to allow each motor to start at different times after power returns to normal to avoid overloading the power system. This ensures that no two motors will be drawing startup current levels at the same time. This timer is initiated when acceptable power is applied to the L1, L2, L3 terminals, and will also be reloaded if the incoming power does not meet the LV, HV, or VUB settings when the motor is not running. When power returns to within these settings, the RD0 timer will count down and close the relay. If RD0 timer is set to 0, this timer will be disabled.
Note on D22: RD1 is referred to as the rapid-cycle timer, in seconds. The purpose of this timer is to provide protection against short cycling of the controls between motor starts. This timer is initiated after the motor has been stopped by breaking the control power. At this time the control relay is opened and the output relay will energize (the NO will close) as soon as RD1 timer expires. If RD1 is set to zero this delay will be disabled.
Note on D23: RD3 is referred to as the underload restart timer, in seconds. RD3 is used to restart the motor after an operating motor trips due to UC or LKW. An example of the use of this timer is to set it to the period of time required for a well to recover. This setting varies widely by application and there is no typical setting.
Note on D24: RD2 is referred to as the motor cool-down timer, in seconds. RD2 is used to restart the motor after an operating motor trips due to OC, CUB, or HKW.

## Type of data Frame
SL no: | Type of communications | Way to communicatins
1 | ALL measured value send | STM32 to ESP32
2 | Individual measured send | STM32 to ESP32
3 | fault data | STM32 to ESP32
4 | All trip setup data frame | ESP32 to STM32
5 | Individual trip setup frame | ESP32 to STM32
6 | Display setup frame | ESP32 to STM32
7 | Individual display setup frame | ESP32 to STM32

## FFT
| Odd harmonics | 1,3,5,7,9,11,13,15,17,19,21,23,25,27,29,31,33,35,37,39
R Phase Voltage | 20 | 2 bytes each
Y Phase Voltage | 20 | 2 bytes each
B Phase Voltage | 20 | 2 bytes each
R Phase Current | 20 | 2 bytes each
Y Phase Current | 20 | 2 bytes each
B Phase Current | 20 | 2 bytes each
40*6
240

## Trip message container
Class | Parameter | Enable/ Disable | Auto reset | Trip code | Relay 1 | Relay 2 | Trip Set value | Alarm set value | Time delay | Mode of Setting | <~~~ Copy setup parameters
Trip value | Trip count | Pickup value | Trip time | Trip date
All measurement container
All setup container

## Self diagnostic err codes
Vref error | Err1
ELr processor comm error | Err2
PTC processor comm error | Err3
ESP 32 to STM error | Err4

## Measurements
Class | Parameter | Display | Display representation | Min/Max Theoretical | Resolution | AWS transmission period | 485 Address | 485 number format | 485 R/w
Vol | RY | LED/ BT |  | 5.0V - 20,000.0V | 0.1V | 5 Sec |  |  | R | Voltage (RY,YB,BR)
| YB | LED/ BT |  | 5.0V - 20,000.0V | 0.1V | 5 Sec |  |  | R | Current (R, Y, B)
| BR | LED/ BT |  | 5.0V - 20,000.0V | 0.1V | 5 Sec |  |  | R | Freq
Current | R | LED/ BT |  | 0.05A - 5,000.00A | 0.01 A | 5 Sec |  |  | R | Motor status
| Y | LED/ BT |  | 0.05A - 5,000.00A | 0.01 A | 5 Sec |  |  | R | kW per phase
| B | LED/ BT |  | 0.05A - 5,000.00A | 0.01 A | 5 Sec |  |  | R | kVA per phase
Power | kW | LED/ BT |  | 1 - 10^8 W | 1 W | 5 Sec |  |  | R | kVAr per phase
| kVA | LED/ BT |  | 1 - 10^8 VA | 1 VA | 5 Sec |  |  | R
| kVAr | BT |  | 1 - 10^8 VAr | 1 VAr | 5 Sec |  |  | R
| P.F. | BT |  | 0.200 Lag - 0.200 Lead | 0.001 | 1 Min |  |  | R
| MD kW | BT |  | 1 - 10^8 W | 1 W | 1 Min |  |  | R | Max vol 20kv
| MD kVA | BT |  | 1 - 10^8 VA | 1 VA | 1 Min |  |  | R | Max cur 5k A
Energy | kWh | BT |  | 0.000 - 999999.000 kWh | 0.001 kWh | 1 Min |  |  | R | 100000000
| kVAh | BT |  | 0.000 - 999999.000 kVAh | 0.001 kVAh | 1 Min |  |  | R | 100
Misc | % thermal | LED/ BT |  | 0 - 100 % | 1% | 1 Min |  |  | R
| % load bargraph | LED/ BT |  | 0 - 100 % | 1% | 1 Min |  |  | R
| Leakage (mA) | LED/ BT |  | 5mA - 10000 mA | 1mA | 1 Min |  |  | R
| Freq | LED/ BT |  | 45.00Hz - 55.00Hz | 0.01 Hz | 5 Sec |  |  | R
| Motor status | BT |  | On/Starting/Overload/Trip/Off |  | 5 Sec |  |  | R
| Trip counter | BT |  | 0- 10^7 Operations | 1 | 1 Min |  |  | R
| Stop counter | BT |  | 0- 10^7 Operations | 1 | 1 Min |  |  | R
| Start counter | BT |  | 0- 10^7 Operations | 1 | 1 Min |  |  | R
| Time | BT |  | HH:MM:SS | 1 sec | 1 Min |  |  | R
| Date | BT |  | DD:MM:YYYY | 1 day | 1 Min |  |  | R
Note on B17: This % kW of the rated load